## Slide 1
Declaration of Construction Completion
and
Verification of Readiness to Test
Pam Marks, FPD, DOE-SR
March 2, 2016
Salt Waste Processing Facility
Project No. 05-D-405 (Savannah River Site- Aiken, SC)

## Slide 2: Purpose and Objective
To provide an overview of the contract requirements and processes implemented to ensure the Salt Waste Processing Facility (SWPF) has attained a state of Construction Completion
To provide assurance that DOE and the contractor have a high level of confidence that the facility components and systems, processes, people and paper are in place to commence testing

## Slide 3: Declaration of Construction Completion – Contract Requirements
Modification 116 to contract DE-AC09-02R22210 established the criteria for Declaration and Acceptance of Construction Completion for SWPF
Completion of SWPF facility construction in accordance with the technical baseline diagrams and drawings to include:
  Design Criteria Database
  Basis of Design (Process and Balance of Plant)
  Process Flow Diagrams
  Piping and Instrumentation Drawings
  General Arrangement Drawings
  Electrical Single Line
  HVAC Diagrams
  Radiation Zone Diagrams
  Material Handling Mechanical Flow Diagrams

## Slide 4
Facilities within the scope of the Construction Completion milestone include:
  Central Process Area (CPA)
  Caustic-Side Solvent Extraction (CSSX)
  Alpha Finishing Facility (AFF)
  Cold Chemical Area (CCA)
  Analytical Laboratory
  Diesel Generator Area
  Compressor Building
  Northern and Eastern Facility Support Areas
  Waste Transfer Lines to the designated tie in points
Declaration of Construction Completion – Contract Requirements (cont.)
SWPF CCA Work Area – February 24, 2016

## Slide 5
Requires construction installation, checks and tests to be complete for System Operational Testing (SOT) activities to begin.
Requires Commissioning Planning to be completed (Rev. 00 SOT, Integrated System Operability Test (ISOT) and Calibration, Grooming & Alignment (CG&A) procedures)
Turnover Process governed by PP-CM-8103 “SWPF System Turnover from Construction to Commissioning and Testing Organization”
71 Systems identified in PP-CM-8103
Turnover Acceptance Forms (SWPF-436) documented for all 71 systems
10 day notification required for all initial and final system turnover walk downs
No open “A” punchlist items (“A” items = inoperable equipment required for component of system testing; items affecting safe completion of component or system testing)
Manageable list of “B” punchlist items (“B” items = minor elements of work which do not prevent the utilization of the facility, in part of in whole; items that do not impact system or component operability or safety)
Declaration of Construction Completion – Contract Requirements (cont.)

## Slide 6
Final acceptance of the Construction Completion Milestone is determined by the Federal Project Director (FPD) and Contracting Officer (CO)
Contractor will declare in writing that construction has been completed per contract requirements
DOE has 5 days to determine the reasonableness of the declaration
  Upon DOE acceptance that the declaration is “reasonable”, the cost incurred and completion date become fixed for purposes of fee determination.
DOE has 30 days from the determination of reasonableness to formally accept or reject the Contractor’s declaration.
  In the event DOE rejects the declaration, all costs to resolve findings are not reimbursable.
Declaration of Construction Completion – Contract Requirements (cont.)

## Slide 7: Declaration of Construction Completion – Parsons’ Letter to DOE
Parsons’ Letter to DOE for Declaration of Construction Completion will contain:
Completed SWPF-436 Turnover Acceptance forms
List of System Turnover Package Submittals
Summary Table of Open ‘B’ Items by System, including evidence of a manageable list
Confirmation that open non-conformance reports and Construction Requests for Information have been evaluated and dispositioned to the appropriate ”A” or “B” punchlist
Confirmation Engineering Open Items have been either closed or captured on the appropriate punchlist
Confirmation CG&A procedures have been prepared, and SOT and ISOT procedures have been completed to Revision 0 fulfilling CLIN 0005AC scope of work
  Listing of CG&A procedures
  Listing of Revision 0 SOT and ISOT procedures
Parsons’ final cost and schedule values for incentive fee calculations
This declaration excludes:
  Final Waste Transfer Line tie-in
  Administration Building
  Items turned back to construction during the start-up testing phase

## Slide 8
Parsons’ System Turnover Process
AT SWPF

## Slide 9: Parsons Turnover Process
Contract recognizes PP-CM-8103, “System Turnover from Construction to Commissioning” as establishing the requirements for system turnover.
Parsons System Turnover Process addresses:
  Roles and Responsibilities
  The Turnover Package
  The Turnover Process
  The Transfer of Jurisdictional Control from Construction to Commissioning and Testing
  Guidance for a turn-back process used for construction work such as testing reveals a need for design change or latent defect.

## Slide 10: Parsons Turnover Process
0
Punchlist Item Categorization
Final Walkdown
(10 day notification required)
Prepare Turnover Package
Initial Walkdown
(10 day notification required)
Complete “A”
Punchlist Items
Jurisdictional Control is Transferred
Work Off “B” Punchlist Items
Manageable List at Construction Completion
71 Systems Turned Over

## Slide 11: Parsons Turnover Process – Prepare Turnover Package
Preparation of a Turnover Package
Construction assembles the Turnover Package
18 sections in every Turnover Package
  Applicable/Not Applicable sections are identified
Turnover Package draft sent out for review at initial walkdown
Quality Assurance (QA) reviews the package for completeness and accuracy
Turnover Package approved by Commissioning Manager after Final Walkdown

## Slide 12: Parsons Turnover Process – Initial Walkdown
Construction, Cognizant System Engineer (CSE), and Commissioning and Testing (C&T) required for Initial Walkdown
Purpose of Initial Walkdown:
  Determines system readiness for Turnover
  Confirms System Turnover Boundaries
  System Boundary Drawings are under configuration control
  Master set of Boundary Drawings that ensures no gaps between systems
  Identifies punchlist items
Quality Assurance (QA), Operations (OPS), Environment, Safety & Health (ESH), and DOE are notified
  DOE attends all Initial Walkdowns
10 Day formal notification required
Weekly System Planning Meeting
Manages punchlist item closure
Walkdown scheduling
DOE attends
  Identifies punchlist items
Initial Walkdown Electrical Panel Checkout

## Slide 13: Parsons Turnover Process – Punchlist Item Categorization
Parsons Commissioning Manager is the single point of decision for Punchlist Categorization
Categorization of Punchlist items is based on Definitions in “System Turnover from Construction to Commissioning” procedure (PP-CM-8103)
“A” Punchlist Items are required to be complete prior to final system turnover walk-down
  “A” punchlist items include: inoperable equipment required for component/system testing; other items necessary for safe completion of component/system testing, and component labeling necessary for system testing
  Responsible organization works the “A” Punchlist Items to completion
  Punchlist items are managed through a configuration controlled database
  Parsons Commissioning & Testing validates the items and closes in the database
  Turnover package updated with closure documentation
Construction Completion Criteria at SWPF incorporates lessons learned from other recent projects (IWTU and DUF6) in that SWPF “A” Punchlist Items must be completed prior to Construction Completion
Initial Walkdown revealed V8380 not restored from testing
(“A” Punchlist Item)

## Slide 14: Parsons Turnover Process – Final Walkdown
  Occurs upon completion of all “A” Punchlist Items
  Construction, Commissioning & Testing (C&T), and Cognizant System Engineer (CSE) are required for Final Walkdown
  Purpose of the Final Walkdown:
    Validate completion of “A” Punchlist Items
    Ensure no additional Punchlist Items
  QA, Operations (OPS), Environment, Safety & Health (ESH), and DOE are notified
    DOE attends all Final Walkdowns
  10 Day formal notification required
Switch is Thrown To Energize SWPF

## Slide 15: Parsons Turnover Process – Transfer of Jurisdictional Control
Director of Construction and Commissioning Manager signs Turnover Package Acceptance Form
  After Initial Walk Down to confirm Turnover Boundaries (Section I)
  After Final Walkdown to acknowledge completion of all “A” Punchlist Items and Jurisdictional Transfer (Section II)
OPS hangs jurisdictional tags after C&T assumes control of a system
  Physical identification preventing further construction activity

## Slide 16: Parsons Turnover Process – Work Off “B” Punchlist Items
Type “B” Punchlist Items are maintained in the punchlist database
“Manageable List” of Type “B” Punchlist Items:
  Resourced to complete within 6 months of construction complete
  Documented and accepted as part of Declaration of Construction Completion
  Demonstrated via a resource loaded schedule
  Completed within the Over Target Baseline budget
Initial Walkdown “B” Item
Handle Not Tightened

## Slide 17
DOE TURNOVER OVERSIGHT
AT SWPF

## Slide 18: DOE Turnover Oversight - Objectives
Understand DOE’s turnover oversight process
  Relationship to the SWPF Certification and Verification Plan (CVP)
  How the process is structured
  Components of the process
  How the components work together
How the turnover oversight process ties to DOE’s concurrence with Parsons’ Declaration of Construction Completion
Walkdown of Lockout to extend Decontaminated Salt Solution Transfer Line

## Slide 19: DOE Turnover Oversight - Relation to CVP
The CVP summarizes DOE Salt Waste Processing Facility Project Office (SWPFPO) Integrated Project Team (IPT) oversight activities leading to Critical Decision 4 (CD-4)
The CVP focuses on 4 Primary Areas:
  Construction Complete (Turnover)
  Component/System Testing
  Operational Verification
  Readiness Validation
Turnover Oversight Process is governed by SWPF-15-DI-001

## Slide 20: DOE Turnover Oversight
Assessmen
t
Turnover Package Review
Walkdowns
Punchlist
Documentation:
Turnover Checklist
Turnover Affirmation
Personnel
Line Management Review Board (LMRB)
All 71 systems go through this process
SWPF Project Office Management

## Slide 21: DOE Turnover Oversight – Personnel
Turnover Personnel assigned for EACH system
  DOE IPT System Lead
    Member of the SWPFPO IPT Construction and Startup (C&SU) Division
    Serves as CVP’s Construction Turnover Specialist
  DOE IPT System Engineering Lead
    Member of SWPFPO ITP Engineering Division
  DOE IPT C&SU Division
    Member of the SWPFPO IPT C&SU Division
Turnover Personnel received training on the DOE oversight procedure
DOE SWPFPO has Subject Matter Experts (SMEs) with experience from other DOE projects (IWTU, DUF6, MOX, DWPF, ARP/MCU)

## Slide 22: DOE Turnover Oversight – Personnel (cont.)
System Responsibility Matrix
  The 71 systems were divided into 12 areas aligned with the Parsons’ CSE assignments
  IPT assigned personnel based on subject area of expertise
    The right people reviewing the right systems
Area | System Turnover ID | Title | DOE IPT Turnover System Lead |  | DOE Design Authority System Lead | 
 |  |  | Primary | Alternate | Primary | Alternate
Electrical | ELEC-00 | Electrical | Bryan | Albright | Tshishiku | Tshishiku
 | DG-00 | Standby Diesel Generator |  |  |  | 
 | UPS-00 | Uninterruptable Power Supply |  |  |  | 
 | PMS-00 | Power Monitoring System |  |  |  | 
BPCS/SIS | ICP-00 | Instrument Control Panels | Bryan | Albright | Vanpeursem | Hewitt
 | BPCS-00 | Basic Process Control System |  |  | Hewitt | Vanpeursem
 | SIS-00 | Safety Instrumented System |  |  |  | 
 | RPS-00 | Radiation Monitoring |  |  |  | Tshishiku
 | CTV-00 | CCTV |  |  |  | 
Plant Air/Gas/Dilution | AIR-00 | Plant Air | Bryan | Mayo | Zalants | Ridley
 | AIR-01 | Plant Air – AFF Segments |  |  |  | 
 | ADS-00 | Air Dilution |  |  |  | 
Material Handling | MHD-00 | Material Handling Equipment | Bryan | Albright | Zalants | Tshishiku

## Slide 23
DOE Turnover Oversight - Turnover Package Review
DOE reviews all turnover packages
Turnover Package review starts prior to initial walk down.
Turnover Package review is completed after the final walk down.
Data is readily available for review via the Parsons Turnover System Summary Database
  Within a few clicks the reviewer has access to actual scanned work documents
  This system should be a best practice in the lessons learned report
The database consists of 12 different databases linked together which allows the system to provide current data

## Slide 24: DOE Turnover Oversight – Turnover Package Review (cont.)
Turnover Package Reviewers
  Turnover System Lead (SL)
    Sections 1-4, 15-18 which cover Administrative sections, system boundaries, maintenance sections, and other
    The SL also combines other reviewers’ inputs and prepares and presents the assessment
  Engineering (ENG)
    Sections 5-11 –commodities (valve list, line list, specialty items, equipment and cables)
    Includes design and installation of the system to ensure they are consistent with the system description in the Preliminary Documented Safety Analysis (PDSA)
  Construction and Start Up (C&SU)
    Sections 12-14 work packages/quality records
    Documentation of field work complete as well as applicable Construction Acceptance Testing

## Slide 25: DOE Turnover Oversight – Walkdowns/Punchlist
Initial and Final Walkdowns
  DOE participates in ALL Initial and Final System Walkdowns
  System Lead participates in and document the formal walkdowns
  QA participates as requested
Process Improvements since implementation
  Improved formality for conduct of walkdowns
  Partnering walkdowns between DOE oversight and Commissioning and Testing Group prior to Initial and/or Final Walkdowns
  DOE oversees validation of Type “A” Punchlist Items as they are completed
Contactors turned over December 11, 2015

## Slide 26: DOE Turnover Oversight – Documentation
Turnover Checklist:
  SWPF-15-DI-001, Attachment 1, DOE Turnover Oversight Guidance, identifies criteria for review of each turnover activity/package section
  Reviews are conducted on a sampling basis
  Sample size takes into account Safety Significant (SS) Items, Mission Critical Nature of the System, and Hazards and Risks

## Slide 27: DOE Turnover Oversight – Documentation (cont.)
Checklist
  Captures all activities performed by all reviewers
    Includes all document reviews
    Includes observations of the Contractor’s walkdowns, reviews, and other turnover activities
    Includes identified issues and resolution
  Managed and maintained by the System Lead
  All reviewers provide input to the Checklist

## Slide 28: DOE Turnover Oversight – Documentation (cont.)
Turnover Affirmation:
  Provides declaration of Initial and Final Walkdown participation
  Provides declaration that the turnover package review was completed
  Signed by System Lead (SL) and System Engineering Lead (ENG)
  Is the recommendation of DOE Commissioning & Start-up (C&SU) Director to Federal Project Director and Contracting Officer that the system is Construction Complete

## Slide 29: DOE Turnover Oversight – Assessment
  Summarizes the system turnover review efforts
  Provides a records repository for the Checklist and Affirmation
  Documents any findings identified during system turnover oversight and review
  Is presented to the Line Management Review Board (LMRB)

## Slide 30: DOE Turnover Oversight - Line Management Review Board (LMRB)
Provides a forum for DOE management review of selected readiness documents to ensure that integrated readiness oversight activities adequately assess the overall achievement of operational readiness
The LMRB was established early to utilize the senior management oversight concept for turnover
Key Members
  SWPF Federal Project Director (LMRB Chair)
  SRS Deputy Site Manager (Executive Advisor)
  DOE-SR Chief Engineer
  Assistant Manager for Waste Disposition
  Assistant Manager for Nuclear Materials Stabilization
  Assistant Manager for Infrastructure and Environmental Stewardship
  Director for Office of Safety and Quality Assurance
  SWPF DOE Headquarters Liaison
  Ad Hoc Appointees as needed

## Slide 31: DOE Turnover Oversight – Other Activities
Verification of Disposition of all Engineering Open Items
The DOE FPD has directed Parsons to resolve all DOE identified findings to DOE’s satisfaction prior to declaring Construction Completion.
  Oversight of Permanent Power Electrical Energization
Conducted Vendor/Supplier source oversight and on-site inspections of sampled Structures, Systems, and Components (SSC) installation. Deficiencies have been identified in hardware and documentation for Parsons’ resolution.
Verified pedigrees of ASME Large Vessels, Caustic-Side Solvent Extraction (CSSX) contactors and skids, including factory testing
Verified Quality Data Packages & Work Packages for High Level Waste Transfer Lines
Reviewed ~95% of all weld radiographs of ASME Piping Systems taken since 2013, and is reviewing a sample of Dark Cell weld radiographs from years 2009 – 2012
Resolved electrical inspection issues (bend radius)

## Slide 32
Readiness to Test

## Slide 33: Readiness to Test – Initial Testing
SOT/ISOT Approval
  Test procedures are reviewed by Contractor and DOE concurrently
  Review comments are dispositioned through the Joint Test Group (JTG).
  Test procedures are sent to Commissioning Review Board (CRB) for approval.
    FPD is a voting member of the CRB
There are 60 SOTs and 5 ISOTs
  Approval of all test procedures is a condition of Declaration of Construction Completion

## Slide 34: Readiness to Test – Parsons’ Personnel Staffing to Support Testing
Staffing of Commissioning and Test personnel on track to support the commencement of testing in late April/May (25 of 31 positions filled to date).
Operations staffing in place to provide support of the Testing program (54 of 54 filled).
Maintenance staffing in place to support testing. Additional hiring is anticipated to provide future maintenance needs. (28 hired to support testing).
Parsons recently hired 2 senior managers with extensive readiness and commissioning experience (Bob Traynor and Jerry Long)
  Parsons recently added experienced Readiness and Startup Leadership for support of the MSA-1, Transition to Testing (Bob Parks)
Control Room Simulator Training at Parsons’ Technology Center

## Slide 35: Readiness to Test – Parsons’ Management Self-Assessment-1
This MSA is the first in a series of MSAs to be performed in the project path to Critical Decision 4 (CD-4)(Approve Start of Operations or “Project Completion”)
MSA-1 will evaluate the Project’s readiness to conduct the System Testing program.
The focus of MSA-1 will serve as the basis for the Project Manager’s Approval to Commence Testing.
The performance objectives and assessment criteria are limited to those necessary for System Testing and related Work Control.
MSA-1 was initiated February 8, 2016 and will conclude on April 1, 2016
DOE is conducting oversight of MSA-1

## Slide 36: Pathway to Readiness Success
Integrated Baseline Review (IBR) ensured realistic and achievable baseline to achieve CD-4
    First of a Kind review in DOE
Chemical Simulants to be used during Cold Commissioning
ARP/MCU and Parsons' Technology Center testing to continue until SWPF start-up
Hired DOE Readiness Review Coordinator early in the Project (4 years prior to scheduled CD-4)
Developing a Plan of Action (POA) early in the Project (18 months ahead of schedule)
    Incorporated Lessons Learned from other projects
    Shared readiness expectations and lessons learned early with Contractor
    POA Scoping meetings conducted with Contractor
Implemented oversight CVP during construction phase of the Project
    Developed 8-hour CVP Training course for Integrated Project Team members
    Contractor participated in CVP Training
Implemented resource-loaded project schedule of DOE Readiness activities which is tied to the Contractor Project schedule
Cognizant System Engineers in place and provisionally qualified

## Slide 37: Pathway to Readiness Success (cont.)
Initiated LMRB early in the Project
    Independent Board comprised of senior DOE managers responsible for reviewing various readiness deliverables (e.g., Turnover Packages, Readiness Affirmations, Program Documents for DOE approval, etc.)
SWPFPFO personnel regularly attend Contractor Planning, Scheduling, and Project Status meetings
    Establish a continuous presence in the field
    Focus on working closely with Contractor to resolve issues as they are identified
Contractor to perform 3 MSAs
  Readiness to Test (MSA-1);
  Ready for Cold Commissioning (MSA-2);
  Ready to proceed into the Contractor Operational Readiness Review (CORR) (MSA-3)
  DOE provides oversight for all MSAs
DOE will conduct independent Integrated Safety Management System (ISMS) Assessments. Final verification of ISMS implementation will be part of Operational Readiness Reviews.

## Slide 38: Acronym List
AFF Alpha Finishing Facility
ARP Actinide Removal Process
ASME American Society of Mechanical Engineers
C&SU Construction & Start Up
C&T Commissioning & Testing
CCA Cold Chemical Area
CD-4 Critical Decision-4
CG&A Calibration, Grooming & Alignment
CO Contracting Officer
CORR Contractor’s Operational Readiness Review
CPA Central Processing Area
CRB Commissioning Review Board
CSE Cognizant System Engineer
CSSX Caustic Side Solvent Extraction
C&SU Construction & Start-up
CVP Certification and Verification Plan
DOE Department of Energy
DUF6 Depleted Uranium Hexafluoride
DWPF Defense Waste Processing Facility
ENG Engineering
ES&H Environment, Safety and Health
FPD Federal Project Director
IPT Integrated Project Team
ISMS Integrated Safety Management System
ISOT Integrated System Operability Test
IWTU Integrated Waste Treatment Unit
JTG Joint Test Group
LMRB Line Management Review Board
MCU Modular Caustic-Side Solvent Extraction Unit
MOX Mixed Oxide Facility
MSA Management Self Assessment
OPS Operations
OTB Over-Target Baseline
POA Plan of Action
PP-CM Project Procedure Commissioning
QA Quality Assurance
SL System Lead
SME Subject Matter Expert
SOT System Operability Test
SS Safety Significant
SSC Safety Significant Components
SWPF Salt Waste Processing Facility
SWPFPO Salt Waste Processing Facility Project Office
WTL Waste Transfer Line

## Slide 39
Back up / supporting slides

## Slide 40: List of 71 Systems - Crosswalk – Turnover System to SOT to CSE 1/26/2016 – Green shading, Walkdown Complete

## Slide 41: List of 71 Systems (cont.)

## Slide 42: List of 71 Systems (cont.)

## Slide 43: SWPF Current Status of System Turnover
Use Chart from Monthly to HQ
Accepted by DOE thru 2/24/16

## Slide 44: Readiness to Test - MSA-1 Team
MSA-1 Team Members | Assigned Area | DOE Oversight
Bob Parks | Team Leader | Mac Hogle
Bob Traynor | Testing, Plant Staffing | Jeff Howell (TE, PS)
Brad Swanson | Work Planning and Control, Maintenance Implementation | Rodney Walker (WP, MI)
Leah Lavalle | Emergency Management, Conduct of Operations, Procedure Development and Verification | Duane Delmore (EM) Irvin Rubin (CO and PD)
Jerry Long | Quality Assurance, Software Quality Assurance, Cyber Security | Herman Kunis (QA) Jacob Miller (SQ) Marcus Saint Jean (CY)
Tom Helms | Training and Qualification, Integrated Safety Management System, Environmental | Roger Battles (TQ) Scotti Fryar (ISMS) Armanda Watson (Envr.)
Bill Brasel | Fire Protection, Engineering, Configuration Management | James Harris (FP) Richard Rustad (EN, CM)
Mike Pittman | Occupational Safety and Health Chemical Safety | Gina Price (SH, CS)